## Arkusz1
Group | Parameter | Description | Type | Unit | Nesta 120 FS | Nesta 160 FS | Nesta 200 FS | Nesta 250 FS
Parameters describe the type of construction data
Data | Type | Type of appliance, e.g. Space heating, Indirect hot water, Other generator, Not known, Unset. | Text | N/A | Space heating | Space heating | Space heating | Space heating
Data | Shape | Characteristic shape of product. | Text | N/A | Rectangular (Vertical) | Rectangular (Vertical) | Rectangular (Vertical) | Rectangular (Vertical)
Data | Safety_Valve_Connection_Type | Safety valve connection type, e.g. Flanged, Plain, Threaded, Other, Not know, Unset | Text | N/A | Threaded | Threaded | Threaded | Threaded
Data | Mounting | The way the appliance is mounted, e.g. Floor standing, Wall mounted, Other, Not know, Unset | Text | N/A | Floor Standing | Floor Standing | Floor Standing | Floor Standing
Data | HeaterOperation | The heater operation, e.g. Non condensing, Condensing, Other, Not know, Unset | Text | N/A | Condensing | Condensing | Condensing | Condensing
Data | Heat_Exchanger_Material | Heat exchanger material, e.g. Aluminium, Cast iron, Copper, Stainless Steel, Steel, Other, Not know, Unset | Text | N/A | Stainless Steel | Stainless Steel | Stainless Steel | Stainless Steel
Data | Fuel_Connection_Type | Condensate drain type e.g. Flanged, Plain, Threaded, Other, Not Known, Uns | Text | N/A | Threaded | Threaded | Threaded | Threaded
Data | Flue_or_Air_Intake_Classification | Flue/air intake classification standard, e.g. 'B23' | Text | N/A | B23; B23P; C43; C53; C63; C83 | B23; B23P; C43; C53; C63; C83 | B23; B23P; C43; C53; C63; C83 | B23; B23P; C43; C53; C63; C83
Data | Flow_and_Return_Connection_Type | Choose flow/return connection type e.g. Flanged, Plain, Threaded, Other, Not Known, Unse | Text | N/A | Threaded | Threaded | Threaded | Threaded
Data | Finish | An alphanumeric value representing the characteristic primary finish of the product, e.g. Anodised, Brushed, Painted, Natural (Self-finish) | Text | N/A | Painted | Painted | Painted | Painted
Data | External_Material | Choose main external material e.g. Steel, Plastic, Foil covered insulation, Aluminium, Other, Not Known, Unset | Text | N/A | Aluminium | Aluminium | Aluminium | Aluminium
Data | Drain_Connection_Type | Choose drain connection type, e.g. Flanged, Plain, Threaded, Other, Not Known, Unset | Text | N/A | Threaded | Threaded | Threaded | Threaded
Data | Configuration | Choose configuration of appliance; e.g. Single boiler, Multiple boilers, Cascade boilers, Other, Not Known, Unset | Text | N/A | Single boiler | Single boiler | Single boiler | Single boiler
Data | Condensate_Drain_Type | Choose condensate drain type e.g. Flanged, Plain, Threaded, Other, Not Known, Unse | Text | N/A | Plain | Plain | Plain | Plain
Data | Colour | Characteristic or primary color of product | Text | N/A | grey | grey | grey | grey
Data | Burner_Control_Type | e.g. On/Off, High/Low, Modulating, Other, Not known, Unset | Text | N/A | Modulating | Modulating | Modulating | Modulating
Parameters describe the type of electrical data
Electrical | Voltage | Voltage | Digit | Volts | 230.000000000000 | 230.000000000000 | 230.000000000000 | 230.000000000000
Electrical | Supply_Phase | Enter incoming supply phase, e.g. 1, 3. | Text | N/A | 1 | 1 | 1 | 1
Electrical | Starting_Current | Enter maximum starting current. | Text | Amps | n/a | n/a | n/a | n/a
Electrical | Minimum_Power_Consumption | Enter minimum power consumption. | Text | W | 22 W | 30 W | 28 W | 30 W
Electrical | Maximum_Power_Consumption | Enter maximum power consumption. | Text | W | 178 W | 197 W | 208 W | 275 W
Electrical | IP_Rating | Enter appliance enclosure rating. Ingress Protection rating e.g. IP56 | Text | N/A | IPX4D | IPX4D | IPX4D | IPX4D
Electrical | IK_Rating | Enter appliance enclosure rating. Impact resistance rating. | Text | N/A | n/a | n/a | n/a | n/a
Electrical | Fuse_Rating | Enter fuse rating. | Text | Amps | 6.3 A | 6.3 A | 6.3 A | 6.3 A
Electrical | Full_Load_Current | Enter current at full load. | Text | Amps | n/a | n/a | n/a | n/a
Electrical | Frequency | Enter incoming supply electrical frequency, e.g. N/A, DC, 50,60, Other, UserDefined | Text | Hertz | 50 Hz | 50 Hz | 50 Hz | 50 Hz
Parameters describe the type of performance data
General | Water_Treatment_Required | State whether product requires water treatment. If yes, refer to manufacturer's instructions. |  |  | Yes | Yes | Yes | Yes
General | Turndown_Ratio | Enter turndown ratio. Ratio of maximum to minimum fire. | Text | N/A | 11:1 | 8:1 | 8:1 | 10:1
General | Sound_Pressure_Level | Enter sound pressure level at 1m | Text | dBA | n/a | n/a | n/a | n/a
General | Rated_Output | Product rated output | Text | W | 120W | 160W | 200W | 250W
General | Rated_Criteria | Enter rated criteria, e.g. 50/30, 80/60, Other, Not Known, Unset. | Text | N/A | 80/60 | 80/60 | 80/60 | 80/60
General | Primary_Fuel | Type of fuel used, e.g. Gas - Biogas, Gas - NG, Gas - LPG, Gas - Other, Oil - 28/sec, Oil - 35/sec, Oil - Bioliquid, Oil - Heavy, Oil - Other, Not Known, Unset. | Text | N/A | Gas - NG | Gas - NG | Gas - NG | Gas - NG
General | Optional_Fuel | Type of fuel used (dual fuel only), e.g. No Optional Fuel, Gas - Biogas, Gas - NG&#xD&#xA, Gas - LPG, Gas - Other, Oil - 28/sec, Oil - 35/sec, Oil - Bioliquid, Oil - Heavy, Oil - Other, Not Known, Unset. If Not Applicable, type 'No Optional Fuel' | Text | N/A | Gas - LPG | Gas - LPG | Gas - LPG | Gas - LPG
General | Oil_Consumption_rate | Enter fuel consumption - oil. If Not Applicable Mark '0'. | Text | N/A | 0 | 0 | 0 | 0
General | Nominal_Oil_Inlet_Pressure | Enter nominal oil pressure. Standard oil inlet pressure. If Not Applicable Mark '0'. | Text | mbar | 0 | 0 | 0 | 0
General | Nominal_Gas_Inlet_Pressure | nter nominal inlet gas pressure. Standard gas inlet pressure. If Not Applicable Mark '0'. | Text | mbar | 20 mbar | 20 mbar | 20 mbar | 20 mbar
General | NOx_Emissions | Enter NOx emission. NOx Emissions at 0% O2 | Text | mg/kWh | 36.6 | 39.4 | 38.7 | 36.0
General | Minimum_Operating_Pressure | Enter minimum operating pressure of appliance. Water side. | Text | bar | 0.8 bar | 0.8 bar | 0.8 bar | 0.8 bar
General | Minimum_Oil_Inlet_Pressure | Enter minimum inlet oil pressure. Minimum safe oil inlet pressure. If Not Applicable Mark '0'. | Text | mbar | 0 | 0 | 0 | 0
General | Minimum_Gas_Inlet_Pressure | Enter minimum inlet gas pressure. Minimum safe gas inlet pressure. If Not Applicable Mark '0'. | Text | mbar | 17 bar | 17 bar | 17 bar | 17 bar
General | Minimum_Flow_Rate_At_20C_Temperature_Differential | Minimum flow rate at 20ºC Δt. | Text | l/s | 1.53 l/s | 2.00 l/s | 2.50 l/s | 3.08 l/s
General | Minimum_Flow_Rate_At_11C_Temperature_Differential | Minimum flow rate at 11ºC Δt. | Text | l/s | n/a | n/a | n/a | n/a
General | Maximum_Operating_Pressure | Enter maximum operating pressure of appliance. Water side. | Text | bar | 6 bar | 6 bar | 6 bar | 6 bar
General | Maximum_Oil_Inlet_Pressure | Enter maximum inlet oil pressure. Maximum safe oil inlet pressure. If Not Applicable Mark '0'. | Text | mbar | 0 | 0 | 0 | 0
General | Maximum_Gas_Inlet_Pressure | Enter maximum inlet gas pressure. Maximum safe gas inlet pressure. If Not Applicable Mark '0'. | Text | mbar | 25 bar | 25 bar | 25 bar | 25 bar
General | Hydraulic_Resistance_at_20C_temperature_differential | Hydraulic Resistance at 20ºC Δt. | Text | mbar | 80 mbar | 88 mbar | 101 mbar | 109 mbar
General | Hydraulic_Resistance_at_11C_temperature_differential | Hydraulic Resistance at 11ºC Δt. | Text | mbar | n/a | n/a | n/a | n/a
General | Gas_Consumption_rate | Enter fuel consumption - gas. If Not Applicable Mark '0' | Text | m3/h | 44387 | 44269 | 44245 | 44460
General | Erp_Seasonal_Efficiency | Enter ErP seasonal efficiency. Seasonal Efficiency, below 70kW. If Not Applicable Mark '0' | Text | % | 0.93 | 0.93 | 0.93 | 0.93
General | ErP_Rated_Efficiency_at_Part_Load | Enter efficiency at part load. Gross Rated Efficiency at 30% Load, above 70kW. If Not Applicable Mark '0' | Text | % | 96.9 % | 96.9 % | 96.9 % | 97.0 %
General | ErP_Rated_Efficiency_at_Full_Load | Enter efficiency at full load. Gross Rated Efficiency at 100% Load, above 70kW. If Not Applicable Mark '0' | Text | % | 88.1 % | 88.2 % | 88.0 % | 88.1 %
General | ErP_Energy_Label | State ErP efficiency class. If Not Applicable Mark '0' | Text | N/A | 0 | 0 | 0 | 0
General | Building_Regulations_Seasonal_Efficiency | Enter building regulations seasonal efficiency. | Text | N/A | n/a | n/a | n/a | n/a
Parameters describe the type of manufacturer data. Revit requires classification code, the Keynote and Assembly Code should be assigned to each family type so that it understands the object type and how it should display and behave in a project.
Identity Data | URL | Hyperlink to manufacturer’s website. | URL | N/A | www.myaic.eu | www.myaic.eu | www.myaic.eu | www.myaic.eu
Identity Data | Type comments
Identity Data | Referenced_Standard | BS, EN, ISO | Text | N/A | EN 15502-1/EN 15502-2-1 | EN 15502-1/EN 15502-2-1 | EN 15502-1/EN 15502-2-1 | EN 15502-1/EN 15502-2-1
Identity Data | Product_Range | Enter full name of product range | Text | N/A | Nesta FS | Nesta FS | Nesta FS | Nesta FS
Identity Data | Product_Model_Number | Enter full manufacturers product code | Text | N/A | N 120 FS | N 160 FS | N 200 FS | N 250 FS
Identity Data | Product_Literature | Internet address for further details of this product. | URL | N/A | https://myaic.eu/wp-content/uploads/2019/03/A-070336_B_EN-Nesta-120-250_1305_regular.pdf | https://myaic.eu/wp-content/uploads/2019/03/A-070336_B_EN-Nesta-120-250_1305_regular.pdf | https://myaic.eu/wp-content/uploads/2019/03/A-070336_B_EN-Nesta-120-250_1305_regular.pdf | https://myaic.eu/wp-content/uploads/2019/03/A-070336_B_EN-Nesta-120-250_1305_regular.pdf
Identity Data | Producent | Name of originating manufacturer | Text | N/A | AIC Europe BV | AIC Europe BV | AIC Europe BV | AIC Europe BV
Identity Data | Description | An alphanumeric value giving a concise description of the construction product represented by the BIM object. (Manufacturer objects shall include factual information only including manufacturer trade and catalogue name). | Text | N/A | A high efficiency condensing boiler; perfect for single or multiple boiler installations in medium to large buildings including schools; hotels; care homes; offices and commercial buildings. | A high efficiency condensing boiler; perfect for single or multiple boiler installations in medium to large buildings including schools; hotels; care homes; offices and commercial buildings. | A high efficiency condensing boiler; perfect for single or multiple boiler installations in medium to large buildings including schools; hotels; care homes; offices and commercial buildings. | A high efficiency condensing boiler; perfect for single or multiple boiler installations in medium to large buildings including schools; hotels; care homes; offices and commercial buildings.
Identity Data | Manufacturer_Website | Hyperlink to manufacturer’s website. | URL | N/A | www.myaic.eu | www.myaic.eu | www.myaic.eu | www.myaic.eu
Identity Data | Manufacturer | Name of originating manufacturer | Text | N/A | AIC Europe BV | AIC Europe BV | AIC Europe BV | AIC Europe BV
Identity Data | Model | Manufacturer model number. | Text | N/A | N 120 FS | N 160 FS | N 200 FS | N 250 FS
Identity Data | Keynote | Enter the NBS reference appropriate for the family content. Refer to the NBS website for a list of classification codes | Text | N/A
Identity Data | CE_Approval | Number, Yes, No | Text | N/A | Yes | Yes | Yes | Yes
Identity Data | Assembly code | For Assembly Code, click in the Value field, and click the browse button to select the appropriate Assembly Code from the dialogues. | Text | N/A | D3020100 | D3020100 | D3020100 | D3020100
IFC parameters will increase the effectiveness of the ‘Revit to IFC’ export process. Revit handles the minimum IFC parameter requirements upon export to IFC, however by adding the parameters below it will improve accuracy and interoperability with other platforms where the exported IFC may be utilised.
IFC Parameters | NominalLength | Typically the larger or primary horizontal dimension. | Lenght | mm | 648 | 648 | 648 | 648
IFC Parameters | NominalHeight | Typically the vertical or secondary characteristic dimension. | Lenght | mm | 1524 | 1524 | 1524 | 1524
IFC Parameters | NominalDepth | Nominal width of product, typically the characteristic or secondary horizontal or characteristic dimension. | Lenght | mm | 787 | 787 | 859 | 859
IFC Parameters | IfcExportType | The IFC export Type | Text | N/A | Pset_BoilerTypeCommon | Pset_BoilerTypeCommon | Pset_BoilerTypeCommon | Pset_BoilerTypeCommon
IFC Parameters | IfcExportAs | The Export type | Text | N/A | IfcBoilerType | IfcBoilerType | IfcBoilerType | IfcBoilerType
The following parameters with the prefix "_" must be added to the model if model will be uploaded at bimstore. The following parameters with the prefix "NBS" should be added to the content to allow minimum compatibility with NBS specification products. NBS is a UK-based system of construction specification used by architects and other building professionals to describe the materials, standards and workmanship of a construction project.
Model Properties | _DistributedBy | This should read “www.bimstore.co.uk” | URL | N/A | www.bimstore.co | www.bimstore.co | www.bimstore.co | www.bimstore.co
Model Properties | _CurrentRevision | This parameter should be maintained when editing and updating families. This should start at 1 and progress per family revision. | Integer | N/A | 1 | 1 | 1 | 1
Model Properties | _CreatedBy | This should read “www.bimstore.co.uk” or your own URL if created in-house. | URL | N/A | www.myaic.eu | www.myaic.eu | www.myaic.eu | www.myaic.eu
Model Properties | _BimSpecGuid | Leave this field blank, this will be completed by bimstore. This is used by bimstore to identify this component and link it with property dimensions in bimstore and other future software packages. | Integer | N/A | 0 | 0 | 0 | 0
Model Properties | _BSBibleVersion | Version of bimstore Bible with which content is compliant | Integer | N/A | 16 | 16 | 16 | 16
Model Properties | _Author | This should be the name of the person who made the original family and should not be changed when the family is revised. You may use a URL in this field to link to a company website, if appropriate. | Text | N/A | DaPr | DaPr | DaPr | DaPr
Model Properties | NBSReference | Alphanumeric value of the appropriate NBS clause reference from https://toolkit.thenbs.com. This shall be in the format xx-yy-zz/nnn where xx-yy-zz is the NBS section code and nnn is the 3 digit NBS clause number. | Text | N/A | 90-40-05/340 | 90-40-05/340 | 90-40-05/340 | 90-40-05/340
Model Properties | NBSOfficeMasterTag | Always put n/a | Text | N/A | n/a | n/a | n/a | n/a
Model Properties | NBSObjectName | The name of the object as it will appear in NBS Create | Text | N/A | AIC_GasFiredCondensingBoiler | AIC_GasFiredCondensingBoiler | AIC_GasFiredCondensingBoiler | AIC_GasFiredCondensingBoiler
Model Properties | NBSNote | Leave Blank | Text | N/A
Model Properties | NBSDescription | Alphanumeric value of the appropriate NBS clause title from https://toolkit.thenbs.com. If the value is not known or not available, the property shall be completed with ‘n/a’. | Text | N/A | n/a | n/a | n/a | n/a
Model Properties | BIMObjectName | Object name as per section 5.1. Do not include file extension (e.g. .RVT) | Text | N/A | AIC_Boiler_Nesta_FS_120-250 | AIC_Boiler_Nesta_FS_120-250 | AIC_Boiler_Nesta_FS_120-250 | AIC_Boiler_Nesta_FS_120-250
All bimstore content must have the correct COBie parameters. These parameters are used to create COBie Information Exchanges (a standard format Excel file) that can be utilised by third party software and organisations. Construction Operation Building information exchange. A structured facility information for the commissioning, operation and maintenance of an asset. Parameters describe the type of controls, operations and warranty
Other | WarrantyStartDate | Completed with the default value ‘1900-12-31T23:59:59’. | Text | Date
Other | WarrantyGuarantorParts | A valid email address for the organisation responsible for supplying or manufacturing the construction project. | URL | N/A | info@myaic.eu | info@myaic.eu | info@myaic.eu | info@myaic.eu
Other | WarrantyDurationUnit | Completed with the value ‘year’. | Text | N/A | years | years | years | years
Other | WarrantyDurationParts | Duration of parts warranty. | Integer | Year | 0 | 0 | 0 | 0
Other | WarrantyDescription | Alphanumeric value providing a description of the warranty content and exclusions. | Text | N/A
Other | SerialNumber | The serial number assigned to an occurrence of a product by the manufacturer. | Blank | N/A | 0 | 0 | 0 | 0
Other | Overall_Width | Geometrical parameter. Enter overall width of appliance. | Lenght | mm | 648.000000000000 | 648.000000000000 | 648.000000000000 | 648.000000000000
Other | Overall_Length | Geometrical parameter. Enter overall depth or lenght of appliance. | Lenght | mm | 787.000000000000 | 787.000000000000 | 859.000000000000 | 859.000000000000
Other | Overall_Height | Geometrical parameter. Enter overall height of appliance. | Lenght | mm | 1524.000000000000 | 1524.000000000000 | 1524.000000000000 | 1524.000000000000
Other | ModelReference | An alphanumeric value for the name of the manufactured item as used by the manufacturer. | Text | N/A | Nesta FS | Nesta FS | Nesta FS | Nesta FS
Other | ModelNumber | An alphanumeric value representing product, item or unit number assigned by manufacturer. | Text | N/A | N 120 FS | N 160 FS | N 200 FS | N 250 FS
Other | Material | Characteristic or primary material of product | Text | N/A | Aluminium; steel; stainless steel; polymers | Aluminium; steel; stainless steel; polymers | Aluminium; steel; stainless steel; polymers | Aluminium; steel; stainless steel; polymers
Other | ManufactureName | Name of originating manufacturer | Text | N/A | AIC Europe BV | AIC Europe BV | AIC Europe BV | AIC Europe BV
Other | Interlocks | This is the system which allows your thermostat and programmer to tell the boiler when to turn on and off. | Text | N/A | Yes | Yes | Yes | Yes
Other | InstallationDate | The date that the manufactured item was installed | Blank | N/A
Other | Gross_Weight | Enter weight of appliance during operation. | Text | kg | 0 | 0 | 0 | 0
Other | ExpectedLife | The expected serviceable lifetime, or the acceptable period of use of a product. It is the time that any manufactured item can be expected to be ‘serviceable’ or supported by its manufacturer. | Text | Year
Other | DurationUnit | Completed with the value ‘year’. | Text | N/A | years | years | years | years
Other | CreatedOn | Object creation date, 2017-02-26 T09:00:00 | Text | N/A
Other | CreatedBy | The name of the person, organisation or library provider that created the object. | Text | N/A | info@myaic.eu | info@myaic.eu | info@myaic.eu | info@myaic.eu
Other | Control_Type | Energy-saving controls that the boiler contains.e.g. Weather compensating, Optimised Start/Stop, On/Off, Programmer (7 day), Room thermostat, Programmable room thermostat | Text | N/A | Weather compensating; Optimised Start/Stop; On/Off | Weather compensating; Optimised Start/Stop; On/Off | Weather compensating; Optimised Start/Stop; On/Off | Weather compensating; Optimised Start/Stop; On/Off
Other | ClassifcationValue | Classifications value of the object | Text | N/A | Pr_60_60_08_34 | Pr_60_60_08_34 | Pr_60_60_08_34 | Pr_60_60_08_34
Other | ClassifcationName | Name of the classification system e.g. Uniclass2015 | Text | N/A | Uniclass2015 | Uniclass2015 | Uniclass2015 | Uniclass2015
Other | BarCode | The identity of the bar code (or rfid) given to an occurrence of the product. | Text | N/A
Other | BMS_Links | Connecting the appliance to the building management system. Type Y or N | Text | N/A | Yes | Yes | Yes | Yes
Other | AssetType | Alphanumeric default value of ‘fixed’ or ‘movable’. Fixed representing equipment attached and integral to building function (eg. Heating, plumbing, elevators) and movable for standalone equipment (eg. a lamp, a table). | Text | N/A | Fixed | Fixed | Fixed | Fixed
Other | AssetIdentifier | Completed with an alphanumeric default value ‘n/a’. | Text | N/A
Parameters describing the specific dimensions
Text | Water_Content | Water content | Text | litres | 51 liters | 47 liters | 66 liters | 62 liters
Text | Shipping_Weight | Enter shipping weight of product with packaging. | text | kg | 215 | 240 | 250 | 270
Text | Safety_Valve_Connection_Size | Enter safety valve connection size. | Text | mm/inches | G1"" | G1"" | G1"" | G1""
Text | Fuel_Connection_Size | Enter fuel connection size | Text | mm/inches | G3/4"" | G3/4"" | G1"" | G1""
Text | Flue_Connection_Size | Enter flue spigot size. Also state whether internal or external in notes | Text | N/A | 130 mm | 130 mm | 180 mm | 180 mm
Text | Flow_and_Return_Connection_Size | Enter flow/return connection size. | Text | mm/inches | G2"" | G2"" | G2 1/2"" | G2 1/2""
Text | Drain_Connection_Size | Enter drain connection size. | Text | mm/inches | G 1"" | G 1"" | G 1"" | G 1""
Text | Condensate_Drain_Size | Enter condensate drain size. Also state whether internal or external in notes | Text | mm/inches | 25mm | 25mm | 25mm | 25mm
Text | Air_Inlet_Connection_Size | Air inlet spigot size. Also state whether internal or external in notes | Text | mm/inches | 125mm | 125mm | 125mm | 125mm
Parameters that enable graphics relations, e.g.layers on/off
Graphics | Clerance zone visibility | Geometrical parameter | Check box | N/A | 1 | 1 | 1 | 1
Parameters defining the model geometries
Constraints | Total top to bottom clearance | Geometrical parameter | Lenght | mm | 1924.000000000001 | 1924.000000000001 | 1924.000000000001 | 1924.000000000001
Constraints | Total lleft to right clearance | Geometrical parameter | Lenght | mm | 1648.000000000000 | 1648.000000000000 | 1648.000000000000 | 1648.000000000000
Constraints | Total front to back clearance | Geometrical parameter | Lenght | mm | 2130.999999999995 | 2130.999999999995 | 2130.999999999995 | 2130.999999999995
Constraints | Access_Clearance_Top | Geometrical parameter | Lenght | mm | 400.000000000000 | 400.000000000000 | 400.000000000000 | 400.000000000000
Constraints | Access_Clearance_Right | Geometrical parameter | Lenght | mm | 500.000000000000 | 500.000000000000 | 500.000000000000 | 500.000000000000
Constraints | Access_Clearance_Left | Geometrical parameter | Lenght | mm | 500.000000000000 | 500.000000000000 | 500.000000000000 | 500.000000000000
Constraints | Access_Clearance_Front | Geometrical parameter | Lenght | mm | 1000.000000000000 | 1000.000000000000 | 1000.000000000000 | 1000.000000000000
Constraints | Access_Clearance_Bottom | Geometrical parameter | Lenght | mm | 0.000000000000 | 0.000000000000 | 0.000000000000 | 0.000000000000
Constraints | Access_Clearance_Rear | Geometrical parameter | Lenght | mm | 500.000000000000 | 500.000000000000 | 500.000000000000 | 500.000000000000
Dimensions | SupplySide | Geometrical parameter | Lenght | mm | 527.999999999998 | 527.999999999998 | 534.000000000000 | 534.000000000000
Dimensions | SupplyHeight | Geometrical parameter | Lenght | mm | 1097.999999999998 | 1097.999999999998 | 1097.999999999998 | 1097.999999999998
Dimensions | SupplyReturnLenght | Geometrical parameter | Lenght | mm | 731.000000000000 | 731.000000000000 | 753.000000000000 | 753.000000000000
Dimensions | SupplyReturnEnd | Geometrical parameter | Lenght | mm | 100.000000000005 | 100.000000000005 | 122.000000000005 | 122.000000000005
Dimensions | SupplyDiameter | Geometrical parameter | Lenght | mm | 60.300000000000 | 60.300000000000 | 76.100000000000 | 76.100000000000
Dimensions | ReturnSide | Geometrical parameter | Lenght | mm | 159.999999999996 | 159.999999999996 | 151.000000000000 | 151.000000000000
Dimensions | ReturnHeight | Geometrical parameter | Lenght | mm | 354.000000000000 | 354.000000000000 | 361.000000000000 | 361.000000000000
Dimensions | ReturnDiameter | Geometrical parameter | Lenght | mm | 60.300000000000 | 60.300000000000 | 76.100000000000 | 76.100000000000
Dimensions | GasSide | Geometrical parameter | Lenght | mm | 468.999999999998 | 479.000000000000 | 479.000000000000 | 485.000000000000
Dimensions | GasLenght | Geometrical parameter | Lenght | mm | 720.000000000000 | 720.000000000000 | 720.000000000000 | 720.000000000000
Dimensions | GasHeight | Geometrical parameter | Lenght | mm | 1306.999999999999 | 1321.000000000000 | 1309.000000000000 | 1313.000000000000
Dimensions | GasEnd | Geometrical parameter | Lenght | mm | 89.000000000005 | 89.000000000005 | 89.000000000005 | 89.000000000005
Dimensions | GasDiameter | Geometrical parameter | Lenght | mm | 26.900000000000 | 26.900000000000 | 33.700000000000 | 33.700000000000
Dimensions | FlueGasSide | Geometrical parameter | Lenght | mm | 333.999999999996 | 333.999999999996 | 333.999999999996 | 333.999999999996
Dimensions | FlueGasCenter | Geometrical parameter | Lenght | mm | 80.000000000005 | 80.000000000005 | 117.000000000000 | 117.000000000000
Dimensions | FlueGasHeight | Geometrical parameter | Lenght | mm | 98.000000000000 | 98.000000000000 | 98.000000000000 | 98.000000000000
Dimensions | FlueGasDiameter | Geometrical parameter | Lenght | mm | 130.000000000000 | 130.000000000000 | 180.000000000000 | 180.000000000000
Dimensions | CondensateSide | Geometrical parameter | Lenght | mm | 127.999999999996 | 127.999999999996 | 127.999999999996 | 127.999999999996
Dimensions | CondensateLenght | Geometrical parameter | Lenght | mm | 644.000000000000 | 644.000000000000 | 644.000000000000 | 644.000000000000
Dimensions | CondensateHeight | Geometrical parameter | Lenght | mm | 141.000000000001 | 141.000000000001 | 141.000000000001 | 141.000000000001
Dimensions | CondensateEnd | Geometrical parameter | Lenght | mm | 13.000000000005 | 13.000000000005 | 13.000000000005 | 13.000000000005
Dimensions | Condensate_Drain_Diameter | Geometrical parameter | Lenght | mm | 25.000000000000 | 25.000000000000 | 25.000000000000 | 25.000000000000
Dimensions | AirInletSide | Geometrical parameter | Lenght | mm | 166.999999999997 | 166.999999999997 | 166.999999999997 | 166.999999999997
Dimensions | AirInletHeight | Geometrical parameter | Lenght | mm | 1324.000000000000 | 1324.000000000000 | 1324.000000000000 | 1324.000000000000
Dimensions | AirInletEnd | Geometrical parameter | Lenght | mm | 40.000000000005 | 40.000000000005 | 40.000000000005 | 40.000000000005
Dimensions | Air_Inlet_Connection_Diameter | Geometrical parameter | Lenght | mm | 125.000000000000 | 125.000000000000 | 125.000000000000 | 125.000000000000
Dimensions | BoilerWidth | Geometrical parameter | Lenght | mm | 648.000000000000 | 648.000000000000 | 648.000000000000 | 648.000000000000
Dimensions | BoilerHeight | Geometrical parameter | Lenght | mm | 1524.000000000001 | 1524.000000000001 | 1524.000000000001 | 1524.000000000001
Dimensions | BoilerDepth | Geometrical parameter | Lenght | mm | 630.999999999995 | 630.999999999995 | 630.999999999995 | 630.999999999995
Dimensions | AirInletLenght | Geometrical parameter | Lenght | mm | 671.000000000000 | 671.000000000000 | 671.000000000000 | 671.000000000000